NOTICE OF BID

The Town of Oliver Springs is soliciting competitive sealed bids from qualified 
contractors for the Water Treatment Plant Raw Water Pump Station System Improvements.

Bid submittal date and location:

Sealed bids will be received by

The Town of Oliver Springs

Attention: Thomas McCormick, City Manager

717 Main St.

Oliver Springs TN. 37840

Until 2:30 P.M. local time on

December 2, 2020

At that time the bids will be publicly opened and read aloud at 2:30 P.M. and any bid received after 2:30 P.M. will not be accepted. Bid envelope must be marked on the outside and labeled SEALED BID, name of Bidder, date and time of opening. Contractor providing the utility work must have a current valid Contractors License.

Project Description:

Town of Oliver Springs Water Treatment Plant is requesting sealed bids to replace the motors and controls at the Raw Water Pump. These Improvements included in this project include the following Scope of work:

Contractor will remove and replace the (2) Deming pumps and motors and also remove and replace the electrical control panels in the remote pump house used to control these devices. The contractor will add new pumps, motors, couplings, GPM sensor, and automation controls that run the pump motors at a user set-point in GPM and also run the pumps based on hours used. This automation control will be capable of controlling the pumps from both a local (at pump house) and a remote location (control room). At each location a 6" HMI touchscreen will be installed for user interface. Communications between the pump house and control room shall be ethernet using NLOS (non line of site) Ethernet radios.

This project will be 'Turn Key' meaning the Contractor will perform all jobs required to make the pump system upgrade functional. Demolition, mounting and adding new components, complete conduit (where required) and wiring including power, control and field wire, startup and documentation.

Component Listing:

Main Drive Panel mounted in remote pump house:

Nema 12 (36x24x10) with the following mounted, wired and tested.

1 - Automation Direct Productivity 2000 PLC with 24VDC digital I/O and Analog for GPM and drive control

1 - 6" Touchscreen HMI for local pump drive and PLC control and monitoring

2 - ABB 15HP Digital AC Pump drives

2 - Drive disconnects

1 - NLOS ethernet radio and antenna

1 - Industrial Ethernet Switch

1 - Safety Relay Module

1 -Control Transformer

1 - Panel 3-phase lightning arrester

1 - Lot Control breakers, fuses, wire, terminals, labels, wire tray mounted hardware.

Control Room HMI:

1 - 6" Touchscreen HMI for pump drive and PLC control and monitoring at pump house

1 - NLOS ethernet radio and antenna

1 - Industrial Ethernet Switch

1 - Lot Wire, terminals, labels, wire tray mounted hardware.

Pump and Motor Install:

(2) 126350-MBM Deming 5062 pumps mounted to Weg 15HP 1800RPM 254T Frame motors. Sureflex

Coupling will be used to connect motor to pump.

(The pump motor combination shall be laser aligned when mounting)

Supplied loose and field mounted:

1 - Turck GPM flow Sensor with 4-20ma output

All control voltage shall be 24VDC. All new conduit for field wiring shall be intermediate metal conduit (IMC) or sealtite. New motor lead wiring shall be shielded inverter duty cabling, Ethernet wiring shall be Cat-6 shielded.

Site visit required

Water Plant contact:

Leslie Lowe, Chief Operator

805 Oliver Springs Hwy

Clinton, TN. 37716.

865-457-4298

Facility Access

The Town of Oliver Springs does not discriminate on the basis of disability in the admission or access to its programs or activities. Any requests for reasonable accommodations required by individuals to fully participate in any open meeting, program or activity should be directed to Thomas McCormick, City Manager, 865-435-7722.

Instructions on Submitting Questions

Questions regarding bids should be submitted to Thomas McCormick at fax 865-435-4881, or email oscitymanager@comcast.net no later than 3:00 p.m. local time, November 30, 2020. Bids are legal and binding upon the bidder when submitted.

Bid Withdrawal:

No Bidder may withdraw his Bid within sixty (60) days after the actual date of the opening thereof.

The Town of Oliver Springs will award the Contract to the lowest and/or best "qualified" bidder, subject with the Owner's right to reject any or all bids, to waive technicalities, and to make an award deemed in its best interests. With limited response, Oliver Springs reserves the right to extend the solicitation opening date as appropriate in order to assure a competitive procurement process.

TOWN OF OLIVER SPRINGS RAW WATER PUMP STATION SYSTEM IMPROVEMENTS

II. GENERAL BACKGROUND (PRIME CONTRACTOR)

- Current name and address of Applicant: _______________________________

1.	Applicant Name: ___________________________________________
Mailing Address: ___________________________________________
City:		___________________________________________

State and Zip:	____________________________________________

Business Address: __________________________________________
City:		___________________________________________

State and Zip: 	____________________________________________

Contact Person: 	___________________________________________
Telephone and Fax: _________________________________________
E-mail:		___________________________________________

2.	Applicant is: Licensed to conduct utility business in the State of Tennessee?

YES_
No	_

If Yes, Provide Applicants State of Tennessee 
Contractors Licenses Number: _____________________________________

- Principals/Officers/Individuals authorized to sign contracts:

Name and Title: _____________________________________________ 
Name and Title: _____________________________________________
Name and Title: _____________________________________________

Bid Form

Water Treatment Plant Raw Water Pump Station System Improvements

2:30 P.M., December 2nd, 2020

717 Main St.

Oliver Springs, TN. 37840

The removal and replacement of (2) Deming pumps and motors and also the removal and replacement of the electrical control panels in the remote pump house used to control these devices. The contractor will add new pumps, motors, couplings, GPM sensor, and automation controls that run the pump motors at a user set-point in GPM and also run the pumps based on hours used. This automation control will be capable from both a local (at pump house) and a remote location (control room). At each location a 6" HMI touchscreen will be installed for user interface. Communications between the pump house and control room shall be ethernet using NLOS (non line of site) Ethernet radios.

This project will be 'Turn Key' meaning the Contractor will perform all jobs required to make the pump system upgrade functional. Demolition, mounting and adding new components, complete conduit (where required) and wiring including power, control and field wire, startup and documentation.

Total Project Bid                      					  $________________

Company Name   _____________________________________

Signature	  ______________________________________

Name (Print)	  ______________________________________